## Sheet1
Node | Building Type | No. of Unit | Demand/Unit (gpd) | Total Demand (gpd) | Peak Flow (LPS) | Fire Flow (LPS) | Ground Level (m) | HSL (m) | HGL(Peak Flow)(m) | HGL (Fire Flow) (m) | Residual Pressure (Peak Flow) (m) | Residual Pressure (Fire Flow) (m) | Average Flow (LPS) | Residual Pressure (Average Flow) (m) | HGL(Average Flow)(m)
1 | - | - | - | - | 25.00001 | 32.70000 | 32.763 | - | 50.000 | 50.000 | - | - | Not Run | - | Not Run
2 | - | - | - | 0.000 | -0.00000 | -0.00000 | 33.218 | 33.218 | 48.605 | 47.706 | 15.387 | 14.488 | Not Run | Not Run | Not Run
3 | - | - | - | 0.000 | -0.00000 | -0.00000 | 35.301 | 35.301 | 45.528 | 42.647 | 10.226 | 7.345 | Not Run | Not Run | Not Run
4 | - | - | - | 0.000 | -0.00000 | -0.00000 | 35.310 | 35.310 | 45.376 | 42.397 | 10.066 | 7.087 | Not Run | Not Run | Not Run
5 | - | - | - | 0.000 | -0.00000 | -0.00000 | 33.515 | 33.515 | 42.591 | 37.819 | 9.076 | 4.304 | Not Run | Not Run | Not Run
6 | - | - | - | -190,053.352 | -25.00001 | -10.00000 | 33.361 | 33.361 | 42.375 | 37.463 | 9.015 | 4.103 | Not Run | Not Run | Not Run
7 | School | 15000 | 11 | 165,000.000 | 0.00000 | -22.70000 | 33.289 | 33.289 | 42.375 | 34.733 | 9.087 | 1.445 | Not Run | Not Run | Not Run