# General Settings

| Title |  |
| --- | --- |
| No. of Pipes | 6 |
| No. of Nodes | 7 |
| Max Unbal (LPS) | 0.0002 |
| Headloss Formula | Hazen-Williams |
| Fire Flow Water Demand (LPS) | 22.7 |
| Peak Factor | See individual node input |
| Fire Flow factor | See individual node input |
| Max Headloss (Peak Flow) (m/km) | 2 |
| Min Residual Pressure (Peak Flow) (m) | 7.5 |
| Max Residual Pressure (Peak Flow) (m) | 30 |
| Max Headloss (Peak Flow) (m/km) | 2 |
| Min Residual Pressure (Peak Flow) (m) | 7.5 |
| Max Residual Pressure (Peak Flow) (m) | 30 |

# Input Data

## Pipes

| Pipe No | From Node | To Node | Pipe Type | Length (m) | Outer Diameter (mm) | Inner Diameter (mm) | HWC |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | 2 | MS | 59.466 | 150 | 150 | 100 |
| 2 | 2 | 3 | MS | 131.194 | 150 | 150 | 100 |
| 3 | 3 | 4 | MS | 6.464 | 150 | 150 | 100 |
| 4 | 4 | 5 | MS | 118.710 | 150 | 150 | 100 |
| 5 | 5 | 6 | MS | 9.210 | 150 | 150 | 100 |
| 6 | 6 | 7 | MS | 139.174 | 150 | 150 | 100 |

## Nodes

| Node No | Node Head | Additional Node Head | Water Demand (LPS) | Highest Supply Level (m) | Peak Factor | Fire Factor |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 50 | 0 | - | - | 2.500 | 1.000 |
| 2 | - | - | 0.00000 | 33.21816 | 2.500 | 1.000 |
| 3 | - | - | 0.00000 | 35.30118 | 2.500 | 1.000 |
| 4 | - | - | 0.00000 | 35.30999 | 2.500 | 1.000 |
| 5 | - | - | 0.00000 | 33.51520 | 2.500 | 1.000 |
| 6 | - | - | -10.00000 | 33.36079 | 2.500 | 1.000 |
| 7 | - | - | 0.00000 | 33.28868 | 2.500 | 1.000 |

# Peak Flow Calculation

## Pipes Peak Output

| Pipe Mark | Pipe Category | From Node | To Node | Pipe Type | Length (m) | Outer Diameter (mm) | Inner Diameter (mm) | HWC | Flow (LPS) | Velocity (MPS) | Head Loss (m/km) | Head Loss (m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | 1 | 2 | MS | 59.466 | 150 | 150 | 100 | 25.000 | 1.415 | 23.457 | 1.395 |
| 2 |  | 2 | 3 | MS | 131.194 | 150 | 150 | 100 | 25.000 | 1.415 | 23.457 | 3.077 |
| 3 |  | 3 | 4 | MS | 6.464 | 150 | 150 | 100 | 25.000 | 1.415 | 23.457 | 0.152 |
| 4 |  | 4 | 5 | MS | 118.710 | 150 | 150 | 100 | 25.000 | 1.415 | 23.457 | 2.785 |
| 5 |  | 5 | 6 | MS | 9.210 | 150 | 150 | 100 | 25.000 | 1.415 | 23.457 | 0.216 |
| 6 |  | 6 | 7 | MS | 139.174 | 150 | 150 | 100 | -0.000 | 0.000 | 0.000 | 0.000 |

## Nodes Peak Output

| Node No | Flow (LPS) | Ground Level (m) | Highest Supply Level (m) | HGL (m) | Residual Pressure @ GL (m) | Residual Pressure @ HSL (m) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 R | 25.000 | 32.763 | - | 50.000 | - | - |
| 2 | -0.000 | 33.218 | 33.218 | 48.605 | 15.387 | 15.387 |
| 3 | -0.000 | 35.301 | 35.301 | 45.528 | 10.226 | 10.226 |
| 4 | -0.000 | 35.310 | 35.310 | 45.376 | 10.066 | 10.066 |
| 5 | -0.000 | 33.515 | 33.515 | 42.591 | 9.076 | 9.076 |
| 6 | -25.000 | 33.361 | 33.361 | 42.375 | 9.015 | 9.015 |
| 7 | 0.000 | 33.289 | 33.289 | 42.375 | 9.087 | 9.087 |

# Fire Flow Calculation

## Pipes Fire Output

| Pipe Mark | Pipe Category | From Node | To Node | Pipe Type | Length (m) | Outer Diameter (mm) | Inner Diameter (mm) | HWC | Flow (LPS) | Velocity (MPS) | Head Loss (m/km) | Head Loss (m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | 1 | 2 | MS | 59.466 | 150 | 150 | 100 | 32.700 | 1.850 | 38.569 | 2.294 |
| 2 |  | 2 | 3 | MS | 131.194 | 150 | 150 | 100 | 32.700 | 1.850 | 38.569 | 5.060 |
| 3 |  | 3 | 4 | MS | 6.464 | 150 | 150 | 100 | 32.700 | 1.850 | 38.569 | 0.249 |
| 4 |  | 4 | 5 | MS | 118.710 | 150 | 150 | 100 | 32.700 | 1.850 | 38.569 | 4.578 |
| 5 |  | 5 | 6 | MS | 9.210 | 150 | 150 | 100 | 32.700 | 1.850 | 38.569 | 0.355 |
| 6 |  | 6 | 7 | MS | 139.174 | 150 | 150 | 100 | 22.700 | 1.285 | 19.618 | 2.730 |

## Nodes Fire Output

| Node No | Flow (LPS) | Ground Level (m) | Highest Supply Level (m) | HGL (m) | Residual Pressure @ GL (m) | Residual Pressure @ HSL (m) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 R | 32.700 | 32.763 | - | 50.000 | - | - |
| 2 | -0.000 | 33.218 | 33.218 | 47.706 | 14.488 | 14.488 |
| 3 | -0.000 | 35.301 | 35.301 | 42.647 | 7.345 | 7.345 |
| 4 | -0.000 | 35.310 | 35.310 | 42.397 | 7.087 | 7.087 |
| 5 | -0.000 | 33.515 | 33.515 | 37.819 | 4.304 | 4.304 |
| 6 | -10.000 | 33.361 | 33.361 | 37.463 | 4.103 | 4.103 |
| 7 | -22.700 | 33.289 | 33.289 | 34.733 | 1.445 | 1.445 |