# General Settings

| Title |  |
| --- | --- |
| No. of Pipes | 7 |
| No. of Nodes | 8 |
| Max Unbal (LPS) | 0.0002 |
| Headloss Formula | Hazen-Williams |
| Fire Flow Water Demand (LPS) | 22.7 |
| Peak Factor | See individual node input |
| Fire Flow factor | See individual node input |
| Max Headloss (Peak Flow) (m/km) | 2 |
| Min Residual Pressure (Peak Flow) (m) | 7.5 |
| Max Residual Pressure (Peak Flow) (m) | 30 |
| Low Velocity Limit (Peak Flow) (m/s) | 0.3 |
| High Velocity Limit (Peak Flow) (m/s) | 2 |
| Max Headloss (Peak Flow) (m/km) | 2 |
| Min Residual Pressure (Peak Flow) (m) | 7.5 |
| Max Residual Pressure (Peak Flow) (m) | 30 |
| Low Velocity Limit (Peak Flow) (m/s) | 0.3 |
| High Velocity Limit (Peak Flow) (m/s) | 2 |

# Input Data

## Pipes

| Pipe No | From Node | To Node | Pipe Type | Length (m) | Outer Diameter (mm) | Inner Diameter (mm) | HWC |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | 2 | HDPE | 59.466 | 180 | 163.6 | 120 |
| 2 | 2 | 3 | HDPE | 131.194 | 180 | 163.6 | 120 |
| 3 | 3 | 4 | HDPE | 6.464 | 180 | 163.6 | 120 |
| 4 | 4 | 5 | HDPE | 118.710 | 180 | 163.6 | 120 |
| 5 | 5 | 6 | HDPE | 9.210 | 180 | 163.6 | 120 |
| 6 | 6 | 7 | HDPE | 139.174 | 180 | 163.6 | 120 |
| 7 | 7 | 8 | HDPE | 6.462 | 180 | 163.6 | 120 |

## Nodes

| Node No | Node Head | Water Demand (LPS) | Highest Supply Level (m) | Peak Factor | Fire Factor |
| --- | --- | --- | --- | --- | --- |
| 1 | 50 | - | - | 2.500 | 1.000 |
| 2 | - | 0.00000 | 33.21816 | 2.500 | 1.000 |
| 3 | - | 0.00000 | 35.30118 | 2.500 | 1.000 |
| 4 | - | 0.00000 | 35.30999 | 2.500 | 1.000 |
| 5 | - | 0.00000 | 33.51520 | 2.500 | 1.000 |
| 6 | - | 0.00000 | 33.36079 | 2.500 | 1.000 |
| 7 | - | 0.00000 | 33.28868 | 2.500 | 1.000 |
| 8 | - | -10.00000 | 33.36957 | 2.500 | 1.000 |

# Peak Flow Calculation

## Pipes Peak Output

| Pipe Mark | Pipe Category | From Node | To Node | Pipe Type | Length (m) | Outer Diameter (mm) | Inner Diameter (mm) | HWC | Flow (LPS) | Velocity (MPS) | Head Loss (m/km) | Head Loss (m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | 1 | 2 | HDPE | 59.466 | 180 | 163.6 | 120 | 25.000 | 1.189 | 10.966 HIGH | 0.6521 |
| 2 |  | 2 | 3 | HDPE | 131.194 | 180 | 163.6 | 120 | 25.000 | 1.189 | 10.966 HIGH | 1.4386 |
| 3 |  | 3 | 4 | HDPE | 6.464 | 180 | 163.6 | 120 | 25.000 | 1.189 | 10.966 HIGH | 0.0709 |
| 4 |  | 4 | 5 | HDPE | 118.710 | 180 | 163.6 | 120 | 25.000 | 1.189 | 10.966 HIGH | 1.3017 |
| 5 |  | 5 | 6 | HDPE | 9.210 | 180 | 163.6 | 120 | 25.000 | 1.189 | 10.966 HIGH | 0.1010 |
| 6 |  | 6 | 7 | HDPE | 139.174 | 180 | 163.6 | 120 | 25.000 | 1.189 | 10.966 HIGH | 1.5261 |
| 7 |  | 7 | 8 | HDPE | 6.462 | 180 | 163.6 | 120 | 25.000 | 1.189 | 10.966 HIGH | 0.0709 |

## Nodes Peak Output

| Node No | Flow (LPS) | Ground Level (m) | Highest Supply Level (m) | HGL (m) | Residual Pressure @ GL (m) | Residual Pressure @ HSL (m) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 R | 25.000 | 32.763 | - | 50.000 | - | - |
| 2 | -0.000 | 33.218 | 33.218 | 49.348 | 16.130 | 16.130 |
| 3 | -0.000 | 35.301 | 35.301 | 47.909 | 12.608 | 12.608 |
| 4 | -0.000 | 35.310 | 35.310 | 47.838 | 12.528 | 12.528 |
| 5 | -0.000 | 33.515 | 33.515 | 46.537 | 13.021 | 13.021 |
| 6 | -0.000 | 33.361 | 33.361 | 46.436 | 13.075 | 13.075 |
| 7 | -0.000 | 33.289 | 33.289 | 44.910 | 11.621 | 11.621 |
| 8 | -25.000 | 33.370 | 33.370 | 44.839 | 11.469 | 11.469 |

# Fire Flow Calculation

## Pipes Fire Output

| Pipe Mark | Pipe Category | From Node | To Node | Pipe Type | Length (m) | Outer Diameter (mm) | Inner Diameter (mm) | HWC | Flow (LPS) | Velocity (MPS) | Head Loss (m/km) | Head Loss (m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | 1 | 2 | HDPE | 59.466 | 180 | 163.6 | 120 | 32.700 | 1.556 | 18.030 HIGH | 1.0722 |
| 2 |  | 2 | 3 | HDPE | 131.194 | 180 | 163.6 | 120 | 32.700 | 1.556 | 18.030 HIGH | 2.3654 |
| 3 |  | 3 | 4 | HDPE | 6.464 | 180 | 163.6 | 120 | 32.700 | 1.556 | 18.030 HIGH | 0.1165 |
| 4 |  | 4 | 5 | HDPE | 118.710 | 180 | 163.6 | 120 | 32.700 | 1.556 | 18.030 HIGH | 2.1403 |
| 5 |  | 5 | 6 | HDPE | 9.210 | 180 | 163.6 | 120 | 32.700 | 1.556 | 18.030 HIGH | 0.1661 |
| 6 |  | 6 | 7 | HDPE | 139.174 | 180 | 163.6 | 120 | 10.000 | 0.476 | 2.009 | 0.2796 |
| 7 |  | 7 | 8 | HDPE | 6.462 | 180 | 163.6 | 120 | 10.000 | 0.476 | 2.009 | 0.0130 |

## Nodes Fire Output

| Node No | Flow (LPS) | Ground Level (m) | Highest Supply Level (m) | HGL (m) | Residual Pressure @ GL (m) | Residual Pressure @ HSL (m) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 R | 32.700 | 32.763 | - | 50.000 | - | - |
| 2 | -0.000 | 33.218 | 33.218 | 48.928 | 15.710 | 15.710 |
| 3 | -0.000 | 35.301 | 35.301 | 46.562 | 11.261 | 11.261 |
| 4 | -0.000 | 35.310 | 35.310 | 46.446 | 11.136 | 11.136 |
| 5 | -0.000 | 33.515 | 33.515 | 44.306 | 10.790 | 10.790 |
| 6 | -22.700 | 33.361 | 33.361 | 44.139 | 10.779 | 10.779 |
| 7 | -0.000 | 33.289 | 33.289 | 43.860 | 10.571 | 10.571 |
| 8 | -10.000 | 33.370 | 33.370 | 43.847 | 10.477 | 10.477 |