## General
Title
No. of Pipes | 7
No. of Nodes | 8
Max Unbal (LPS) | 0.0002
Fire Flow Water Demand (LPS) | 22.7
Pipe Flow Error Tolerance | 0.01

## Average Flow
MarkPure | Node No | Average Flow (LPS) | Node Coordinates
1 | 1R | 0 | {234,412.726, 587,309.821}
2 | 2 | 0 | {292,711.525, 575,583.235}
3 | 3 | 0 | {414,940.105, 527,917.939}
4 | 4 | 0 | {417,692.104, 522,068.816}
5 | 5 | 0 | {380,338.862, 409,388.236}
6 | 6 | 0 | {371,145.843, 408,828.637}
7 | 7 | 0 | {246,134.779, 469,997.233}
8 | 8 | -10 | {244,038.260, 476,110.166}
Total | Total | -10

## Pipes for Peak Calculation
PEAK FLOW CALCULATION - COMPARISON OF FLOW RATE (Q), VELOCITY (V), AND HEAD LOSS IN BRANCH AND LOOP NETWORK
BRANCH (DEAD-END) NETWORK
Mark | Pipe Category | From Node | From Node Coordinates | To Node | To Node Coordinates | Pipe Type | Length (m) | Outer Diameter (mm) | Inner Diameter (mm) | HWC | Flow (LPS | Velocity (MPS) | Head Loss (m/km) | Head Loss (m) | Remarks
1 |  | 1 | {234.413, 587.310} | 2 | {292.712, 575.583} | HDPE | 59.4665 | 180 | 163.6 | 120 | 25 | 1.189 | 10.966 | 0.65209 | HeadLoss: HIGH
2 |  | 2 | {292.712, 575.583} | 3 | {414.940, 527.918} | HDPE | 131.1938 | 180 | 163.6 | 120 | 25 | 1.189 | 10.966 | 1.4386 | HeadLoss: HIGH
3 |  | 3 | {414.940, 527.918} | 4 | {417.692, 522.069} | HDPE | 6.4642 | 180 | 163.6 | 120 | 25 | 1.189 | 10.966 | 0.070884 | HeadLoss: HIGH
4 |  | 4 | {417.692, 522.069} | 5 | {380.339, 409.388} | HDPE | 118.7105 | 180 | 163.6 | 120 | 25 | 1.189 | 10.966 | 1.3017 | HeadLoss: HIGH
5 |  | 5 | {380.339, 409.388} | 6 | {371.146, 408.829} | HDPE | 9.21 | 180 | 163.6 | 120 | 25 | 1.189 | 10.966 | 0.10099 | HeadLoss: HIGH
6 |  | 6 | {371.146, 408.829} | 7 | {246.135, 469.997} | HDPE | 139.1739 | 180 | 163.6 | 120 | 25 | 1.189 | 10.966 | 1.5261 | HeadLoss: HIGH
7 |  | 7 | {246.135, 469.997} | 8 | {244.038, 476.110} | HDPE | 6.4625 | 180 | 163.6 | 120 | 25 | 1.189 | 10.966 | 0.070865 | HeadLoss: HIGH
LOOP NETWORK
Mark | Pipe Category | From Node | From Node Coordinates | To Node | To Node Coordinates | Pipe Type | Length (m) | Outer Diameter (mm) | Inner Diameter (mm) | HWC | Flow (LPS | Velocity (MPS) | Head Loss (m/km) | Head Loss (m) | Remarks
1 |  | 1 | {234.413, 587.310} | 2 | {292.712, 575.583} | HDPE | 59.4665 | 180 | 163.6 | 120 | 25 | 1.189 | 10.966 | 0.65209 | HeadLoss: HIGH
2 |  | 2 | {292.712, 575.583} | 3 | {414.940, 527.918} | HDPE | 131.1938 | 180 | 163.6 | 120 | 8.249 | 0.392 | 1.407 | 0.18456
3 |  | 3 | {414.940, 527.918} | 4 | {417.692, 522.069} | HDPE | 6.4642 | 180 | 163.6 | 120 | 8.249 | 0.392 | 1.407 | 0.0090936
4 |  | 4 | {417.692, 522.069} | 5 | {380.339, 409.388} | HDPE | 118.7105 | 180 | 163.6 | 120 | 8.249 | 0.392 | 1.407 | 0.167
5 |  | 5 | {380.339, 409.388} | 6 | {371.146, 408.829} | HDPE | 9.21 | 180 | 163.6 | 120 | 8.249 | 0.392 | 1.407 | 0.012956
6 |  | 6 | {371.146, 408.829} | 7 | {246.135, 469.997} | HDPE | 139.1739 | 180 | 163.6 | 120 | 8.249 | 0.392 | 1.407 | 0.19578
7 |  | 7 | {246.135, 469.997} | 8 | {244.038, 476.110} | HDPE | 6.4625 | 180 | 163.6 | 120 | 8.249 | 0.392 | 1.407 | 0.0090911
8 |  | 2 | {292.712, 575.583} | 8 | {244.038, 476.110} | HDPE | 110.7428 | 180 | 163.6 | 120 | 16.751 | 0.797 | 5.224 | 0.57848 | HeadLoss: HIGH

## Nodes for Peak Calculation
PEAK FLOW CALCULATION - COMPARISON OF RESIDUAL PRESSURE IN BRANCH AND LOOP NETWORK
BRANCH (DEAD-END) NETWORK
MarkPure | Node No | Node Coordinates | Flow (LPS) | Ground Level (m) | HGL (m) | Highest Supply Level (m) | Residual Pressure, GL (m) | Residue Pressure, HSL (m)
1 | 1 R | {234.413, 587.310} | 25 | 32.7633 | 50
2 | 2 | {292.712, 575.583} | 0 | 33.2182 | 49.3479 | 33.2182 | 16.1298 | 16.1298
3 | 3 | {414.940, 527.918} | 0 | 35.3012 | 47.9093 | 35.3012 | 12.6081 | 12.6081
4 | 4 | {417.692, 522.069} | 0 | 35.31 | 47.8384 | 35.31 | 12.5284 | 12.5284
5 | 5 | {380.339, 409.388} | 0 | 33.5152 | 46.5367 | 33.5152 | 13.0215 | 13.0215
6 | 6 | {371.146, 408.829} | 0 | 33.3608 | 46.4357 | 33.3608 | 13.0749 | 13.0749
7 | 7 | {246.135, 469.997} | 0 | 33.2887 | 44.9095 | 33.2887 | 11.6209 | 11.6209
8 | 8 | {244.038, 476.110} | -25 | 33.3696 | 44.8387 | 33.3696 | 11.4691 | 11.4691
LOOP NETWORK
MarkPure | Node No | Node Coordinates | Flow (LPS) | Ground Level (m) | HGL (m) | Highest Supply Level (m) | Residual Pressure, GL (m) | Residue Pressure, HSL (m)
1 | 1 R | {234.413, 587.310} | 25 | 32.7633 | 50
2 | 2 | {292.712, 575.583} | 9.5367e-07 | 33.2182 | 49.3479 | 33.2182 | 16.1298 | 16.1298
3 | 3 | {414.940, 527.918} | 0 | 35.3012 | 49.1634 | 35.3012 | 13.8622 | 13.8622
4 | 4 | {417.692, 522.069} | 0 | 35.31 | 49.1543 | 35.31 | 13.8443 | 13.8443
5 | 5 | {380.339, 409.388} | 0 | 33.5152 | 48.9873 | 33.5152 | 15.4721 | 15.4721
6 | 6 | {371.146, 408.829} | 0 | 33.3608 | 48.9743 | 33.3608 | 15.6135 | 15.6135
7 | 7 | {246.135, 469.997} | 0 | 33.2887 | 48.7785 | 33.2887 | 15.4898 | 15.4898
8 | 8 | {244.038, 476.110} | -25 | 33.3696 | 48.7694 | 33.3696 | 15.3999 | 15.3999

## Pipes for Fire Calculation
PEAK FLOW CALCULATION - COMPARISON OF RESIDUAL PRESSURE IN BRANCH AND LOOP NETWORK
BRANCH (DEAD-END) NETWORK
Mark | Pipe Category | From Node | From Node Coordinates | To Node | To Node Coordinates | Pipe Type | Length (m) | Outer Diameter (mm) | Inner Diameter (mm) | HWC | Flow (LPS | Velocity (MPS) | Head Loss (m/km) | Head Loss (m) | Remarks
1 |  | 1 | {234.413, 587.310} | 2 | {292.712, 575.583} | HDPE | 59.4665 | 180 | 163.6 | 120 | 32.7 | 1.556 | 18.03 | 1.0722 | HeadLoss: HIGH
2 |  | 2 | {292.712, 575.583} | 3 | {414.940, 527.918} | HDPE | 131.1938 | 180 | 163.6 | 120 | 32.7 | 1.556 | 18.03 | 2.3654 | HeadLoss: HIGH
3 |  | 3 | {414.940, 527.918} | 4 | {417.692, 522.069} | HDPE | 6.4642 | 180 | 163.6 | 120 | 32.7 | 1.556 | 18.03 | 0.11655 | HeadLoss: HIGH
4 |  | 4 | {417.692, 522.069} | 5 | {380.339, 409.388} | HDPE | 118.7105 | 180 | 163.6 | 120 | 32.7 | 1.556 | 18.03 | 2.1403 | HeadLoss: HIGH
5 |  | 5 | {380.339, 409.388} | 6 | {371.146, 408.829} | HDPE | 9.21 | 180 | 163.6 | 120 | 32.7 | 1.556 | 18.03 | 0.16606 | HeadLoss: HIGH
6 |  | 6 | {371.146, 408.829} | 7 | {246.135, 469.997} | HDPE | 139.1739 | 180 | 163.6 | 120 | 10 | 0.476 | 2.009 | 0.27964
7 |  | 7 | {246.135, 469.997} | 8 | {244.038, 476.110} | HDPE | 6.4625 | 180 | 163.6 | 120 | 10 | 0.476 | 2.009 | 0.012985
LOOP NETWORK
Mark | Pipe Category | From Node | From Node Coordinates | To Node | To Node Coordinates | Pipe Type | Length (m) | Outer Diameter (mm) | Inner Diameter (mm) | HWC | Flow (LPS | Velocity (MPS) | Head Loss (m/km) | Head Loss (m) | Remarks
1 |  | 1 | {234.413, 587.310} | 2 | {292.712, 575.583} | HDPE | 59.4665 | 180 | 163.6 | 120 | 32.7 | 1.556 | 18.03 | 1.0722 | HeadLoss: HIGH
2 |  | 2 | {292.712, 575.583} | 3 | {414.940, 527.918} | HDPE | 131.1938 | 180 | 163.6 | 120 | 13.7611 | 0.655 | 3.629 | 0.47615
3 |  | 3 | {414.940, 527.918} | 4 | {417.692, 522.069} | HDPE | 6.4642 | 180 | 163.6 | 120 | 13.7611 | 0.655 | 3.629 | 0.023461
4 |  | 4 | {417.692, 522.069} | 5 | {380.339, 409.388} | HDPE | 118.7105 | 180 | 163.6 | 120 | 13.7611 | 0.655 | 3.629 | 0.43085
5 |  | 5 | {380.339, 409.388} | 6 | {371.146, 408.829} | HDPE | 9.21 | 180 | 163.6 | 120 | 13.7611 | 0.655 | 3.629 | 0.033427
6 |  | 7 | {371.146, 408.829} | 6 | {246.135, 469.997} | HDPE | 139.1739 | 180 | 163.6 | 120 | 8.9389 | 0.425 | 1.632 | 0.22719
7 |  | 8 | {246.135, 469.997} | 7 | {244.038, 476.110} | HDPE | 6.4625 | 180 | 163.6 | 120 | 8.9389 | 0.425 | 1.632 | 0.010549
8 |  | 2 | {292.712, 575.583} | 8 | {244.038, 476.110} | HDPE | 110.7428 | 180 | 163.6 | 120 | 18.9389 | 0.901 | 6.557 | 0.72615

## Nodes for Fire Calculation
FIRE FLOW CALCULATION - COMPARISON OF RESIDUAL PRESSURE IN BRANCH AND LOOP NETWORK
BRANCH (DEAD-END) NETWORK
MarkPure | Node No | Node Coordinates | Flow (LPS) | Ground Level (m) | HGL (m) | Highest Supply Level (m) | Residual Pressure, GL (m) | Residue Pressure, HSL (m)
1 | 1 R | {234.413, 587.310} | 32.7 | 32.7633 | 50
2 | 2 | {292.712, 575.583} | 0 | 33.2182 | 48.9278 | 33.2182 | 15.7097 | 15.7097
3 | 3 | {414.940, 527.918} | 0 | 35.3012 | 46.5624 | 35.3012 | 11.2613 | 11.2613
4 | 4 | {417.692, 522.069} | 0 | 35.31 | 46.4459 | 35.31 | 11.1359 | 11.1359
5 | 5 | {380.339, 409.388} | 0 | 33.5152 | 44.3056 | 33.5152 | 10.7904 | 10.7904
6 | 6 | {371.146, 408.829} | -22.7 | 33.3608 | 44.1395 | 33.3608 | 10.7787 | 10.7787
7 | 7 | {246.135, 469.997} | 0 | 33.2887 | 43.8599 | 33.2887 | 10.5712 | 10.5712
8 | 8 | {244.038, 476.110} | -10 | 33.3696 | 43.8469 | 33.3696 | 10.4773 | 10.4773
LOOP NETWORK
MarkPure | Node No | Node Coordinates | Flow (LPS) | Ground Level (m) | HGL (m) | Highest Supply Level (m) | Residual Pressure, GL (m) | Residue Pressure, HSL (m)
1 | 1 R | {234.413, 587.310} | 32.7 | 32.7633 | 50
2 | 2 | {292.712, 575.583} | 0 | 33.2182 | 48.9278 | 33.2182 | 15.7097 | 15.7097
3 | 3 | {414.940, 527.918} | 0 | 35.3012 | 48.4517 | 35.3012 | 13.1505 | 13.1505
4 | 4 | {417.692, 522.069} | 0 | 35.31 | 48.4282 | 35.31 | 13.1182 | 13.1182
5 | 5 | {380.339, 409.388} | 0 | 33.5152 | 47.9974 | 33.5152 | 14.4822 | 14.4822
6 | 6 | {371.146, 408.829} | -22.7 | 33.3608 | 47.9639 | 33.3608 | 14.6031 | 14.6031
7 | 7 | {246.135, 469.997} | 0 | 33.2887 | 48.1911 | 33.2887 | 14.9024 | 14.9024
8 | 8 | {244.038, 476.110} | -10 | 33.3696 | 48.2017 | 33.3696 | 14.8321 | 14.8321